## T2S ETH + Catena
CE+T T2S ETH Modbus TCPIP table - 20170104
Table version 1.0
Catena is mandatory to use this feature. Refer to user manual.
| 600 | Serial number H |  | U16
| 601 | Serial number L |  | U16
| 602 | Application version |  | U16
| 603 | Application revision |  | U16
| 604 | Application built |  | U16
| 605 | Reserved
| 606 | Reserved
| 607 | Reserved
| 608 | Bootloader version |  | U16
| 609 | Bootloader revision |  | U16
| 610 | Bootloader built |  | U16
| 1002 | Total AC output true power | W | S32
| 1004 | Total AC output apparent power | VA | S32
| 1006 | Worse phase load ratio | % | S32
| 1008 | Reserved
| 1010 | Total configured AC output true power | W | S32
| 1012 | Total configured AC output apparent power | VA | S32
| 1014 | Total available AC output true power | W | S32
| 1016 | Total available AC output apparent power | VA | S32
| 1030 | Total AC input true power | W | S32
| 1032 | Total AC input apparent power | VA | S32
| 1034 | Total DC input true power | W | S32
| 1080 | Worse AC output load status |  | U16
| 1081 | Worse AC output hardware status (inverters) |  | U16
| 1082 | Reserved
| 1083 | Reserved
| 1084 | Worse AC input source status |  | U16
| 1085 | Worse AC input hardware status |  | U16
| 1086 | Worse DC input source status |  | U16
| 1087 | Worse DC input hardware status |  | U16
| 1088 | Redundancy lost |  | U16
| 1089 | On DC |  | U16
| 1090 | Reserved |  | U16
| 1091 | MBP engaged |  | U16
| 1096 | Number of events (all alarms types) |  | U16
| 1097 | Number of major alarms |  | U16
| 1098 | Number of minor alarms |  | U16
Output phase 1 | 2050 | Phase 1 true power | W | S32/float
| 2052 | Phase 1 apparent power | VA | S32/float
| 2054 | Phase 1 voltage | V/10 | S32/float
| 2056 | Phase 1 current | A/10 | S32/float
| 2058 | Phase 1 frequency | Hz/100 | S32/float
| 2060 | Reserved
| 2062 | Phase 1 worse power factor | % | S32/float
| 2064 | Phase 1 worse temperature | °C/10 | S32/float
| 2066 | Phase 1 load ratio (W) | % | S32/float
| 2068 | Phase 1 load ratio (VA) | % | S32/float
| 2070 | Phase 1 available true power | W | S32/float
| 2072 | Phase 1 available apparent power | VA | S32/float
Output phase 2 | 2100 | Phase 2 true power | W | S32/float
| 2102 | Phase 2 apparent power | VA | S32/float
| 2104 | Phase 2 voltage | V/10 | S32/float
| 2106 | Phase 2 current | A/10 | S32/float
| 2108 | Phase 2 frequency | Hz/100 | S32/float
| 2110 | Reserved
| 2112 | Phase 2 worse power factor | % | S32/float
| 2114 | Phase 2 worse temperature | °C/10 | S32/float
| 2116 | Phase 2 load ratio (W) | % | S32/float
| 2118 | Phase 2 load ratio (VA) | % | S32/float
| 2120 | Phase 2 available true power | W | S32/float
| 2122 | Phase 2 available apparent power | VA | S32/float
Output phase 3 | 2150 | Phase 3 true power | W | S32/float
| 2152 | Phase 3 apparent power | VA | S32/float
| 2154 | Phase 3 voltage | V/10 | S32/float
| 2156 | Phase 3 current | A/10 | S32/float
| 2158 | Phase 3 frequency | Hz/100 | S32/float
| 2160 | Reserved
| 2162 | Phase 3 worse power factor | % | S32/float
| 2164 | Phase 3 worse temperature | °C/10 | S32/float
| 2166 | Phase 3 load ratio (W) | % | S32/float
| 2168 | Phase 3 load ratio (VA) | % | S32/float
| 2170 | Phase 3 available true power | W | S32/float
| 2172 | Phase 3 available apparent power | VA | S32/float
Input Group 1 Phase 1 | 3030 | Phase true power | W | S32
| 3032 | Phase apparent power | VA | S32
| 3034 | Phase voltage | V/10 | S32
| 3036 | Phase current | A/10 | S32
| 3038 | Phase frequency | Hz/100 | S32
Input Group 1 Phase 2 | 3060 | Phase true power | W | S32
| 3062 | Phase apparent power | VA | S32
| 3064 | Phase voltage | V/10 | S32
| 3066 | Phase current | A/10 | S32
| 3068 | Phase frequency | Hz/100 | S32
Input Group 1 Phase 3 | 3090 | Phase true power | W | S32
| 3092 | Phase apparent power | VA | S32
| 3094 | Phase voltage | V/10 | S32
| 3096 | Phase current | A/10 | S32
| 3098 | Phase frequency | Hz/100 | S32
Input Group 2 Phase 1 | 3150 | Phase true power | W | S32
| 3152 | Phase apparent power | VA | S32
| 3154 | Phase voltage | V/10 | S32
| 3156 | Phase current | A/10 | S32
| 3158 | Phase frequency | Hz/100 | S32
Input Group 2 Phase 2 | 3180 | Phase true power | W | S32
| 3182 | Phase apparent power | VA | S32
| 3184 | Phase voltage | V/10 | S32
| 3186 | Phase current | A/10 | S32
| 3188 | Phase frequency | Hz/100 | S32
Input Group 2 Phase 3 | 3210 | Phase true power | W | S32
| 3212 | Phase apparent power | VA | S32
| 3214 | Phase voltage | V/10 | S32
| 3216 | Phase current | A/10 | S32
| 3218 | Phase frequency | Hz/100 | S32
DC Group 1 | 4000 | Group true power (flowing into system) | W | S32
| 4002 | Group voltage | V/10 | S32
| 4004 | Group current (flowing into system) | A/10 | S32
DC Group 2 | 4060 | Group true power (flowing into system) | W | S32
| 4062 | Group voltage | V/10 | S32
| 4064 | Group current (flowing into system) | A/10 | S32